SPECIFICATION

| INPUT | Voltage Range | 190 - 265VAC |
| --- | --- | --- |
|  | Frequency Range | 50 - 60Hz |
| OUTPUT | Voltage (AC Mode) | 13.8V ±2% |
|  | Voltage (Battery Mode) | Same as battery voltage |
|  | Rated Current | 3A |
|  | Rated Power (Max.) | 52.5W (with 800mA charge current) |
|  | Efficiency (Typ.) | >85% |
|  | Ripple & Noise | <120mVp-p |
|  | Output Channel | 2 channels |
| CHARGING | Voltage | 13.8V ±2% |
|  | Current | 800mA Max |
| PROTECTION | Input | 2A / 250VAC fuse |
|  | Overload | 3.6A ±5%, Hiccup mode, recovers automatically after fault condition is removed. |
|  | Over Voltage | 16V ±5%, Hiccup mode, recovers automatically after fault condition is removed. |
|  | Battery Low Voltage | 10V ±2%, PSU shuts down until AC power recovers. |
|  | Short Circuit | Hiccup mode, recovers automatically after fault condition is removed. |
| ENVIRONMENT | Temperature | Working: -20 - 50℃ | Storage: -30 - 80℃ |
|  | Humidity | Working: 20 - 80%RH | Storage: 10 - 90%RH |
| LED INDICATOR | Red | On | AC power is on |
|  | Green | On | DC output is on |
|  | Yellow | On: Battery is fully charged |
|  |  | Flickering: Battery is charging |
| SAFETY & EMC | EMC Standards | EN 55022: 2010, EN 55024: 2010, EN 61000-3-2: 2014, EN 61000-3-3: 2013 |
|  | LVD Standards | EN 60950-1: 2006 + A11: 2009 + A1: 2010 + A12: 2011 + A2: 2013 |
| METAL BOX & PACKING | Default Metal Box | 205 x 165 x 75mm, fits for 1 pc 12V 7Ah battery. |
|  | Optional Metal Box | 265 x 195 x 75mm, fits for 1 pc 12V 7Ah battery. |
|  |  | 295 x 195 x 90mm, fits for 1 pc 12V 17Ah battery. |
|  | Packing | 41 x 35 x 23.5cm / CTN, 12kg / CTN, 10pcs / CTN (default metal box) |

Access Control Board

|  | ① | PUSH(+) | High-level voltage trigger |
| --- | --- | --- | --- |
|  | ② | PUSH(-) | Low-level voltage trigger |
|  | ③ | SWITCH | Switch signal trigger |
|  | ④ | NC(+) | Normally close 12V output |
|  | ⑤ | NO(+) | Normally open 12V output |
|  | ⑥ | COM | Common terminal of NC(+) and NO(+) |
|  | ⑦ | 12V | 12V output |
|  | ⑧ | GND | Ground |
|  | ⑨ | POTENTIOMETER | 0 - 10s time delayer |

# Text boxes

Description & Features

SIHD1203-01KB is an uninterruptible PSU, its main output is 13.8V / 3A, while it also provides maximum 800mA charge current. It has a special access control board fits for different access systems.

- High efﬁciency up to 85%, long life and high reliability

- Protection: input fuse / overload / over voltage / short circuit

- Multifunction LED indicators

- No delay battery boot up

- 100% full load burn-it test

- Metal box with key-lock, wall mount installation

- Withstand 5G vibration test

- 2 years warranty