SPECIFICATION

| INPUT | Voltage Range | 190 - 265VAC |
| --- | --- | --- |
|  | Frequency Range | 50 - 60Hz |
| OUTPUT | Voltage (AC Mode) | 13.8V ±2% |
|  | Voltage (Battery Mode) | Same as battery voltage |
|  | Rated Current | 5A |
|  | Rated Power (Max.) | 80W (with 800mA charge current) |
|  | Efficiency (Typ.) | >85% |
|  | Ripple & Noise | <120mVp-p |
|  | Output Channel | 1 channel |
| CHARGING | Voltage | 13.8V ±2% |
|  | Current | 800mA Max |
| PROTECTION | Input | 2A / 250VAC fuse |
|  | Overload | 6A ±5%, Hiccup mode, recovers automatically after fault condition is removed. |
|  | Over Voltage | 16V ±5%, Hiccup mode, recovers automatically after fault condition is removed. |
|  | Short Circuit | 10V ±2% |
|  | Battery Low Voltage | 10V ±2%, PSU shuts down until AC power recovers. |
|  | Battery Reverse Connect | Battery not works, no effect on main output. |
| ENVIRONMENT | Temperature | Working: -20 - 50℃ | Storage: -30 - 80℃ |
|  | Humidity | Working: 20 - 80%RH | Storage: 10 - 90%RH |
| LED INDICATOR | Red | On | AC power is on |
|  | Green | On | DC output is on |
|  | Yellow | On: Battery is fully charged |
|  |  | Flickering: Battery is charging |
| SAFETY & EMC | EMC Standards | EN 55022: 2010, EN 55024: 2010, EN 61000-3-2: 2014, EN 61000-3-3: 2013 |
|  | LVD Standards | EN 60950-1: 2006 + A11: 2009 + A1: 2010 + A12: 2011 + A2: 2013 |
| METAL BOX & PACKING | Default Metal Box | 265 x 195 x 75mm, fits for 1 pc 12V 7Ah battery. |
|  | Optional Metal Box | 295 x 195 x 90mm, fits for 1 pc 12V 17Ah battery. |
|  | Packing | 42.5 x 39.5 x 30cm / CTN, 16kg / CTN, 10pcs / CTN (default metal box) |

RELAY ALARM

| ALARM OACR | NO - COM | On | When AC power is on |
| --- | --- | --- | --- |
|  | NC - COM | On | When AC power is off |
| ALARM BLVR | NO - COM | On | When battery voltage > 11V |
|  | NC - COM | On | When 10V < battery voltage < 11V |

# Text boxes

Description & Features

SIHD1205-01BR is an uninterruptible PSU, its main output is 13.8V / 5A, while it also provides constant 800mA charge current and two relay alarm outputs for AC failure / battery low voltage. It could be used for CCTV Surveillance / Access Control / Fire Alarm and other security systems.

- High efﬁciency up to 85%, long life and high reliability

- Protection: input fuse / overload / over voltage / short circuit

- Universal AC input

- Multifunction LED indicators

- No delay battery boot up

- 100% full load burn-it test

- Metal box with key-lock, wall mount installation

- Withstand 5G vibration test

- 2 years warranty